## Slide 1
Parameter | Site Baseline (Peak) | Projected (Site Baseline + Design) | Tariff Limit | Impact ( + / - / = / NA) | Mitigation | New Impact ( + / - / = / NA)
Electricity (kW) | 0 | 0 | 0 | NA | [blank] | NA
Natural Gas (Nm3/month) | 0 | 0 | 0 | NA | [blank] | NA
Water (m3/day) | 0 | 0 | 0 | NA | [blank] | NA
Waste Water (m3/day) | 0 | 0 | 0 | NA | [blank] | NA
Carbon Footprint Scope 1 (tCO2e ) | 0 | 0 | 0 | NA | [blank] | NA
Carbon Footprint Scope 2(tCO2e) | 0 | 0 | 0 | NA | [blank] | 
Energy Assessment Tool completed? | NA
Key Takeaway
System | Site Baseline (Peak) | Projected (Site Baseline + Design) | Redundancy Limit | Redundancy Impact ( + / - / - - / = / NA) | Mitigation | New Impact ( + / - / - - / = / NA)
Boiler, Kg/hr | 0 | 0 | 0 | NA | [blank] | NA
Air Compressor, Nm3/hr | 0 | 0 | 0 | NA | [blank] | NA
Chiller, TR or kW/hr | 0 | 0 | 0 | NA | [blank] | NA
Hot Water, m3/hr | 0 | 0 | 0 | NA | [blank] | NA
CIP Water, m3/hr | 0 | 0 | 0 | NA | [blank] | NA
Production Water, m3/hr | 0 | 0 | 0 | NA | [blank] | NA
Waste Water, m3/hr | 0 | 0 | 0 | NA | [blank] | NA
Is Sustainable Design AES 00.005STD reviewed? | NA
GATE 3 Lite
Utilities and Sustainability Assessment
Delete this text box before FEP presentation
Utilities and Sustainability Assessment
Site Baseline – The entire site peak load inputs from site utilities team
Projected – Site baseline + design load from the project team
Tariff Limit or Redundancy Limit – Inputs from site utilities team
Impact – Review by site utilities manager
Mitigation – Inputs from project team
New Impact – Review by site utilities manager
Notes: 48 times dryer CIP
40 KL per CIP water saving
Temperature increase in 10 deg C
15 KW motor considered for circulation pump.
Electricity Impact
Motor Rated Power – 15 kW
Motor Efficiency – 90%
Peak load per hour – 16.66 kW
Total Power per annum = 48 times dryer CIP x 3 days storage x 24 hours of operation x 16.66 kW = 57577 kWh
Optimized Operation = 48 times dryer CIP x 3 hours of operation before using the recovery water x 16.66 kW + 12 times Sanitization x 4 hours of operation before using the recovery water x 16.66 kW = 3200 kWh tCO2e – 3200 X 0.0007224 = 2.31
Cost Impact – 3200 X 8.5 = 27200 Steam Impact
Water Volume – 40 m3
Delta T for Recovery Water Heating – 20 deg C
PHE efficiency – 95%
Steam to fuel ratio - 13
PHE - 980 kW
Heat required per hour – 40000 X 4.186 X 20 = 3348800/0.95= 3535052 KJ/3600 = 979 kW
Steam, kg at 3 bara = 3535052/2164 = 1633 kg
Natural gas Nm3 = 1633/13 = 125 Nm3
Optimized Natural Gas Monthly = 4 times dryer CIP x 3 x 125 Nm3 = 1500 Nm3
Per Annum = 1500 X 12 = 18000 Nm3
tCO2e = 18000 X 0.00188 = 33.840
Total tCO2e impact = 33.840 + 2.31 = 36.15
Cost Impact = 18000/30 ( 1 MMBTU = 30Nm3) = 600 MMBTU X 2083.32 = 1249992 Rs Water Recovery
Water saved per CIP – 40 m3
Number of Dryer Cip – 48
Sanitizer step water consumption – 110 m3
Number of sanitization per year - 12
Water Saved = (40 X 48)-(110 X 12) = 600 m3 per annum
Cost Saving = 600 X (59(GIDC) + 20(treatment)) = 47400 Rs
Effluent Load Reduction = 600 m3 per annum Cost Saving = 600 x 35 = 21000 Rs
Total Cost Impact = 27200+1249992-47400-21000=1208792/83 =$15 M